NVHR HMI

Software Design Document

Volution Ventilation Group

Document Revision History

| Issue | Date | Authors | Changes |
| --- | --- | --- | --- |
| 0.1 | 17th July 2018 | Hormoz Rebati | Draft Issue |

Referenced Documents

The following items are referenced throughout this document:

| Ref | Document No. | Issue | Description |
| --- | --- | --- | --- |
|  | NVHR GUI (BB NVHR GRAPHICS) | V20 | NVHR HMI Graphics requirements |
|  | Commissioning GUI | V5.3 | Commissioning Screens (Setup Screens) |
|  | NVHR Advanced Controls Spec – BB Control Spec | DRAFT 4 Rev1 | A.K.A. Low Cost Controller – NVHR System |
| 4. | NVHR Advance Controls Protocol at a Glance | V1.0 | EEPROM Memory Map, NVHR Vars and Message from Mainboard to Peripheral and messages from Peripheral to Mainboard |
| 5. | NVHR Advance Controls HMI Home Screen Logic | V 1.03 | The logic for Home Screen states |
| 6. | NVHR Advance Controls Shared hardware IO | V1.0 | NVHR LCC Shared Hardware I/O and Model |

Glossary

| Key | Description |
| --- | --- |
| BACnet | Building Automation Controls Network |
| BB | Breathing Buildings |
| BMS | Building Management System |
| EEPROM | Electrically Erasable Programmable Read-Only Memory |
| GUI | Graphical User Interface |
| HMI | Human Machine Interface |
| MCB | Main Controller Board |
| NVHR | Natural Ventilation with Heat Recovery |
| RTC | Real-Time Clock |
| UART | Universally Asynchronous Receiver/Transmitter |
| UTL | Utility tools |

1.	Introduction	6

1.1	Scope	6

1.1.1	Identification	6

1.1.2	Exclusions	7

1.1.3	SYSTEM Overview	7

1.1.3.1	Overview	7

1.1.3.2	System Context	8

2.	Architectural Design	9

2.1	Software Components	9

2.2	Software Modules	9

2.2.1	Package Diagram	10

2.2.2	Use Case relationships	11

2.2.2.1	Scenario 1 – ordinary user	12

2.2.2.2	Scenario 2 – Maintenance User	12

2.2.2.3	Scenario 3 – Setup (Commissioning) User	13

2.2.3	Dynamic behaviour	14

2.2.3.1	Machine settings and non-volatile memory	14

3.	Software Detail Design and Hierarchy – HMI and COMMS	16

3.1	Communications module	16

3.1.1	Messages from the main board	16

3.1.1.1	Common Header	16

3.1.1.2	Payloads	17

3.1.1.2.1	Payload for MCB_MESSAGE_MEASUREMENTS_1	17

3.1.1.2.2	Payload for MCB_MESSAGE_MEASUREMENTS_2	19

3.1.1.2.3	Payload for MCB_MESSAGE_EE_VALUES_1	20

3.1.1.3	HMI incoming Message data type	22

3.1.2	Messages to the main board	23

3.1.2.1	Message types	23

3.1.2.2	Message Body	23

3.1.2.3	HMI outgoing Message data type	27

3.2	VAR module	28

3.2.1	VAR functionality	29

3.2.2	NVHR Vars	32

3.2.3	NVHR 16 bit EEPROM Memory Map	35

3.3	HMI Software Modules	41

3.3.1	Home screen splash	41

3.3.2	Home screen logic	42

3.3.3	HMI software components	43

3.3.3.1	HMI User_display	44

3.3.3.2	HMI Settings (User_settings)	44

3.3.3.3	HMI User Maintenance	45

3.3.3.4	HMI User Setup	45

3.3.3.5	HMI Common	45

3.3.3.6	HMI System_info	57

3.3.4	Summary	57

3.3.5	Further Work Recommendations	57

4.	HMI Build Tools	58

5.	HMI Build Process	58

6.	Appendix A – NVHR HMI Screens Workflow	59

7.	Appendix B – NVHR HMI Screenshots	63

# Introduction

The Volution Group’s heat recovery and ventilation unit is designed for energy efficient ventilation of school classrooms and offices.

The system is designed for continuous ventilation of rooms within a property, providing significant energy recovery. The features for the current system are specified based on NVHR 1.5. The unit is controlled via touch screen HMI display, WIFI or via a third party building control system (BMS). The touch screen control unit provides the user interface for Setup (commissioning) and Maintenance purposes.

# Scope

# Identification

This document has been produced by Volution Group’s technical design team. The contents constitute the amalgamation of high level and low level software design processes and their components.  This document describes only the software components of the NVHR HMI part of the overall system.

The design of the NVHR system is based on the key engineering deliverables as illustrated below:

The Main NVHR System Key Deliverables

# Exclusions

This document does not contain any software design information for the following components:

- The operating system structure and the NVHR integration

- The login and security procedures

- The Qt framework and Qt Simulator application

- The C/C++/C++11 optimisation features

- Application user guide

- System hardware structure

# SYSTEM Overview

# Overview

The system context diagram below depicts the communication relationship between components of the system. The machine’s mainboard is linked to the remote controls by serial data links.

The remote controls are:

- Wired remote (HMI console)

- WiFi

- BMS

The communication between HMI and Mainboard is by 100-byte Mainboard to remote transmission packets and 84-byte remote to Mainboard replies.  The low level comms are handled by MCB and VAR global modules described later in this document.

# System Context

The following diagram depicts the operational context of the NVHR system along with its interfaces with the external system.

# Architectural Design

The architectural design process is based on the following general requirements:

- The HMI application makes a distinction between the User, Maintenance and the Setup (Commissioning) user modes.  A selective set of operations are available to different category of users:

  - The Ordinary User, no lock code required

  - The Maintenance mode – Pin code required

  - The Setup (Commissioning) mode – Pin code required

- The embedded HMI is based on PIC32MX processor with memory constraints.

- There is a Qt Simulator that is based on PC and Qt graphics library, primarily used for debugging, rapid prototyping and feature functional testing.

- The HMI application communicates to the mainboard (with Processor PIC24FJ) via comms subsystem using a bespoke protocol. See later in this document for further details.

- User training is required to proficiently operate the system

# Software Components

The sections 4 and 5 provide detailed list of the software modules (section 3.3) as well as tools required to build the HMI application.

# Software Modules

This section introduces the high level components and the system behaviour based on the software requirements together with HMI screen flows (appendix A).

# Package Diagram

This section introduces the high level components of BB NVHR, depicting their structural relationship. This enables us to organise the model elements into groups with their global stereotype associations. This is effectively the business architecture diagram. The following diagram represents this structure. The aggregation, composition and dependancy notations represent the object referencing and the object containment strategies.

# Use Case relationships

This section describes the behaviour of the system from the user’s perspective by using actions and reactions. They are derived from the user requirement specification; see NVHR HMI screens workflow in Appendix A. They depict the user interaction with the NVHR HMI sub-system and the environment. Each use case scenario corresponds to the specific type of system use. The system’s functionality is depicted when triggered in response to the simulation of an external actor, such as a system maintainer or an ordinary user.

# Scenario 1 – ordinary user

This scenario “extends” stereotype relationship between the ordinary user without any privileges and the sub-system.  In case of system settings, only the “System Information” is available to the user. This includes, Date, Time, Unit Status, Room Temp Set Point, information about the system (e.g. NVHR Model, Project No).

# Scenario 2 – Maintenance User

Successful pin code entry permits the user to enter the maintenance menu.  This allows system On/Off/Test Sequence performance, System Information, Sensor readings, Set Points Readings, Fan and Damper Status, User Screen options settings, Notices and providing Network information. See appendix B for a complete list of screenshots.

# Scenario 3 – Setup (Commissioning) User

Successful pin code entry enables the user to enter the commissioning menu.  This allows system setup On/Off/Test Sequence performance, System Information, Sensor readings, Set Points Readings, Fan and Damper Status,  User Screen options settings, Notices, providing Network information, setup Night Cool Period, Occupied Days & Hours and more. See appendix B for the screenshots and Appendix A for the HMI screenshot flow diagrams.

# Dynamic behaviour

The machine’s main board is physically linked to the wired HMI system by serial data link. The communication between the two systems is achieved by series of messages using a bespoke protocol. The messages from the main board are 100 bytes and those sent to the board from HMI are 84 bytes.  The serial data is running at 9600 baud rate, 8 data bits, no parity, 1 stop bit, +3.3V TTL level UART signals. The break-down of each package is as follows:

| Transmit Header | 34 bytes | Receive Header | 10 bytes |
| --- | --- | --- | --- |
| Transmit Payload | 64 bytes | Receive Payload | 72 bytes |
| Transmit Checksum | 2 bytes | Receive Checksum | 2 bytes |

The machine broadcasts its messages to all devices at one second interval, timed from the crystal controlled RTC chip. The header information from the board contains all global and common information that is the same for all transmitted messages. However, the payload changes for each message. Generally, a local copy of all non-volatile memory (EE for EEPROM) are stored are stored in HMI. When the user has finished adjusting a particular value, the HMI will send the value back to the main board in an ee write message to be copied in the EE memory.  For details of messages and EE value, see ref 4 (NVHR Advance Controls Protocol at a Glance). The detailed info about the data types responsible for communications is given later in this document. The message types are normally cycled around (from message type 0 to 8, 15).

# Machine settings and non-volatile memory

The machine’s settings are stored in non-volatile memory in the form of EE values. This memory is split into four areas, Working, Defaults, Setup and PCB calibration.

Settings/Working:
	All settings are kept in this area. Any change in setting will be saved here, which will be used in machine’s control logic. The settings need a value when a unit is first used. These are the default values copied from the Defaults area of EE, when a unit is reset to factory defaults.

Defaults:
The defaults are kept in this area. They are loaded in EE from a configuration file using external software. The software:
	Erases this part of EE first
	Copies the default values to Working/Settings area of EE
	It is to these defaults that a ‘reset to factory defaults’ sets the machine.

Set up:
When a machine is first switched on, the serial number, machine type and size are recorded into this section of EE by the external software. This is done only once.

PCB Calibration:
On a brand new board at manufacturing test, test points are measured and adjusted from the diagnostic menu and once in the test limits, the calibration values are recorded into this section. This is done once. The file mcb_ee.h contains the <name> (2 bytes) and the <value> tuple. Each value is written to EE with the message type MCB_MESSAGE_EE_WRITE using mcb_write_reply () function.

# Software Detail Design and Hierarchy – HMI and COMMS

This section will explore in detail, the components, attributes and the methods developed per module, bringing together the overall concept. The instantiation of these modules will provide the NVHR HMI and MCB system.

# Communications module

The communication between HMI and mainboard (MCB) is through this module. The reads and writes to the serial port are carried out through interfaces defined in mcb.c using a bespoke protocol. See ref 4 for more details.

# Messages from the main board

# Common Header

# Payloads

With existing HMI, the following message types are supported – defined in mcb_config.h:

#define MCB_MESSAGE_MEASUREMENTS_1          0u

#define MCB_MESSAGE_MEASUREMENTS_2          1u

#define MCB_MESSAGE_EE_VALUES_1            		 2u

#define MCB_MESSAGE_EE_VALUES_2            		 3u

#define MCB_MESSAGE_EE_VALUES_3             	4u

#define MCB_MESSAGE_EE_VALUES_4             	5u

#define MCB_MESSAGE_EE_VALUES_5            		6u

#define MCB_MESSAGE_EE_VALUES_6             	7u

#define MCB_MESSAGE_EE_VALUES_7             	8u

#define MCB_MESSAGE_EE_ARRAYS_1             	15u

# Payload for MCB_MESSAGE_MEASUREMENTS_1

| 34 | 0 | 1 | Year | 2-digit year (+2000) |
| --- | --- | --- | --- | --- |
| 35 |  | 1 | Month | 1=Jan .. 12=Dec |
| 36 |  | 1 | Day of Month | 1..31 |
| 37 |  | 1 | Day of Week | 1=Monday .. 7=Sunday |
| 38 |  | 1 | Daylight Savings | 0..1 |
| 39 |  | 2 | Hours Run (÷2) | MSB - units of 2 hours |
| 40 |  |  |  | LSB |
| 41 |  | 2 | Hours to next service | MSB |
| 42 |  |  |  | LSB |
| 43 |  | 1 | Commissioning Source | As per override source (x_SERIAL_ID) |
| 44 |  | 1 | OSCTUNE | signed |
| 45 |  | 2 | EE OSCTUNE | MSB |
| 46 |  |  |  | LSB |
| 47 |  | 1 | EE block in use | Block A (79) or block B (217) |
| 48 |  | 2 | EE addr last used | MSB |
| 49 |  |  |  | LSB |
| 50 |  | 2 | Maintenance PIN | MSB |
| 51 |  |  |  | LSB - 0..9999 |
| 52 |  | 2 | Commissioning PIN | MSB |
| 53 |  |  |  | LSB - 0..9999 |
| 54 |  | 2 | Room Temperature (P1) | 0-10V input P1 (T_r = recirc temp) MSB (deg C x10) |
| 55 |  |  |  | LSB |
| 56 |  | 2 | Room CO2 level (P2) | 0-10V input P2 MSB (0..2500ppm) |
| 57 |  |  |  | LSB |
| 58 |  | 2 | Extract NTC thermistor (L) | MSB (deg C x10) |
| 59 |  |  |  | LSB |
| 60 |  | 2 | Mixed NTC thermistor (LC) | MSB (deg C x10) |
| 61 |  |  |  | LSB |
| 62 |  | 2 | External T_e NTC thermistor (RC) | MSB (deg C x10) |
| 63 |  |  |  | LSB |
| 64 |  | 2 | Spare NTC thermistor (R) | MSB (deg C x10) |
| 65 |  |  |  | LSB |
| 66 |  | 1 | Fresh Damper direction | Stopped (0) / Opening (1) / Closing (2) |
| 67 |  | 1 | Fresh Damper drive duration | seconds |
| 68 |  | 1 | Fresh Damper drive stop | seconds |
| 69 |  | 1 | Exhaust Damper direction | Stopped (0) / Opening (1) / Closing (2) |
| 70 |  | 1 | Exhaust Damper drive duration | seconds |
| 71 |  | 1 | Exhaust Damper drive stop sec | seconds |
| 72 |  | 1 | Fresh fan (inner) state |  |
| 73 |  | 1 | Fresh fan endState speed |  |
| 74 |  | 1 | Fresh fan start (parent) | 0..100% |
| 75 |  | 1 | Fresh fan start (child) | 0..100% |
| 76 |  | 1 | Fresh fan end (parent) | 0..100% |
| 77 |  | 1 | Fresh fan state duration | seconds |
| 78 |  | 1 | Fresh fan state elapsed | seconds |
| 79 |  | 1 | Recirc fan (inner) state |  |
| 80 |  | 1 | Recirc fan endState speed |  |
| 81 |  | 1 | Recirc fan start (parent) | 0..100% |
| 82 |  | 1 | Recirc fan start (child) | 0..100% |
| 83 |  | 1 | Recirc fan end (parent) | 0..100% |
| 84 |  | 1 | Recirc fan state duration | seconds |
| 85 |  | 1 | Recirc fan state elapsed | seconds |
| 86 |  | 2 | V1 out (NVHR1.0 Fresh Child) | MSB |
| 87 |  |  |  | LSB |
| 88 |  | 2 | V2 out (NVHR1.0 Recirc Child) | MSB |
| 89 |  |  |  | LSB |
| 90 |  | 2 | L fan PWM (always Fresh Parent) | MSB |
| 91 |  |  |  | LSB |
| 92 |  | 2 | R fan PWM (NVHR1.0 Recirc Parent) | MSB |
| 93 |  |  |  | LSB |
| 94 |  | 2 | L fan RPM (always Fresh Parent) | MSB |
| 95 |  |  |  | LSB |
| 96 |  | 2 | R fan RPM (NVHR1.0 Recirc Parent) | MSB |
| 97 |  |  |  | LSB |

# Payload for MCB_MESSAGE_MEASUREMENTS_2

| 34 | 1 | 2 | Tr_max_today | MSB (deg C x10) |
| --- | --- | --- | --- | --- |
| 35 |  |  |  | LSB |
| 36 |  | 2 | Te_max_today | MSB (deg C x10) |
| 37 |  |  |  | LSB |
| 38 |  | 2 | Assert error triggers | MSB |
| 39 |  |  |  | LSB |
| 40 |  | 1 | Extract T override source | see config.h (x_SERIAL_ID) |
| 41 |  | 1 | Intake T override source | see config.h (x_SERIAL_ID) |
| 42 |  | 1 | Mixed T override source | see config.h (x_SERIAL_ID) |
| 43 |  | 1 | Spare T override source | see config.h (x_SERIAL_ID) |
| 44 |  | 1 | Room T override source | see config.h (x_SERIAL_ID) |
| 45 |  | 1 | Room CO2 override sauce | see config.h (x_SERIAL_ID) |
| 46 |  |  |  |  |
| 47 |  |  |  |  |
| 48 |  |  |  |  |
| 49 |  |  |  |  |
| 50 |  |  |  |  |
| 51 |  |  |  |  |
| 52 |  |  |  |  |
| 53 |  |  |  |  |
| 54 |  |  |  |  |
| 55 |  |  |  |  |
| 56 |  |  |  |  |
| 57 |  |  |  |  |
| 58 |  | 8 | Diag status |  |
| 59 |  |  |  |  |
| 60 |  |  |  |  |
| 61 |  |  |  |  |
| 62 |  |  |  |  |
| 63 |  |  |  |  |
| 64 |  |  |  |  |
| 65 |  |  |  |  |
| 66 |  | 8 | BMS status | Model |
| 67 |  |  |  | Stack State |
| 68 |  |  |  | Traffic Status |
| 69 |  |  |  |  |
| 70 |  |  |  |  |
| 71 |  |  |  |  |
| 72 |  |  |  |  |
| 73 |  |  |  |  |
| 74 |  | 8 | WiFi status | Signal Strength (signed dBm) |
| 75 |  |  |  | remote_status |
| 76 |  |  |  | status |
| 77 |  |  |  |  |
| 78 |  |  |  |  |
| 79 |  |  |  |  |
| 80 |  |  |  |  |
| 81 |  |  |  |  |
| 82 |  | 8 | Wired HMI status |  |
| 83 |  |  |  |  |
| 84 |  |  |  |  |
| 85 |  |  |  |  |
| 86 |  |  |  |  |
| 87 |  |  |  |  |
| 88 |  |  |  |  |
| 89 |  |  |  |  |
| 90 |  | 8 | RF HMI status |  |
| 91 |  |  |  |  |
| 92 |  |  |  |  |
| 93 |  |  |  |  |
| 94 |  |  |  |  |
| 95 |  |  |  |  |
| 96 |  |  |  |  |
| 97 |  |  |  |  |

# Payload for MCB_MESSAGE_EE_VALUES_1

| 34 | 2 | 2 | EE 0 | Number of Values |
| --- | --- | --- | --- | --- |
| 35 |  |  |  |  |
| 36 |  | 2 | EE 1 | Number of Arrays |
| 37 |  |  |  |  |
| 38 |  | 2 | EE 2 | Defaults Version |
| 39 |  |  |  |  |
| 40 |  | 2 | EE 3 | Model |
| 41 |  |  |  |  |
| 42 |  | 2 | EE 4 | Brand |
| 43 |  |  |  |  |
| 44 |  | 2 | EE 5 | Sensors required |
| 45 |  |  |  |  |
| 46 |  | 2 | EE 6 | Spare |
| 47 |  |  |  |  |
| 48 |  | 2 | EE 7 | Spare |
| 49 |  |  |  |  |
| 50 |  | 2 | EE 8 | Language |
| 51 |  |  |  |  |
| 52 |  | 2 | EE 9 | Country |
| 53 |  |  |  |  |
| 54 |  | 2 | EE 10 | Service interval |
| 55 |  |  |  |  |
| 56 |  | 2 | EE 11 | Mainboard setup flags |
| 57 |  |  |  |  |
| 58 |  | 2 | EE 12 | HMI setup flags |
| 59 |  |  |  |  |
| 60 |  | 2 | EE 13 | CO2 Traffic Light Low threshold |
| 61 |  |  |  |  |
| 62 |  | 2 | EE 14 | CO2 Traffic Light High threshold |
| 63 |  |  |  |  |
| 64 |  | 2 | EE 15 | CO2 Traffic Light Colour Selection |
| 65 |  |  |  |  |
| 66 |  | 2 | EE 16 | PID p coefficient |
| 67 |  |  |  |  |
| 68 |  | 2 | EE 17 | PID i coefficient |
| 69 |  |  |  |  |
| 70 |  | 2 | EE 18 | PID d coefficient |
| 71 |  |  |  |  |
| 72 |  | 2 | EE 19 | PID dt |
| 73 |  |  |  |  |
| 74 |  | 2 | EE 20 | 0 |
| 75 |  |  |  |  |
| 76 |  | 2 | EE 21 | 0 |
| 77 |  |  |  |  |
| 78 |  | 2 | EE 22 | 0 |
| 79 |  |  |  |  |
| 80 |  | 2 | EE 23 | 0 |
| 81 |  |  |  |  |
| 82 |  | 2 | EE 24 | 0 |
| 83 |  |  |  |  |
| 84 |  | 2 | EE 25 | 0 |
| 85 |  |  |  |  |
| 86 |  | 2 | EE 26 | 0 |
| 87 |  |  |  |  |
| 88 |  | 2 | EE 27 | 0 |
| 89 |  |  |  |  |
| 90 |  | 2 | EE 28 | 0 |
| 91 |  |  |  |  |
| 92 |  | 2 | EE 29 | 0 |
| 93 |  |  |  |  |
| 94 |  | 2 | EE 30 | BACnet / MODbus Baud Rate + Parity |
| 95 |  |  |  |  |
| 96 |  | 2 | EE 31 | BACnet / MODbus Address |
| 97 |  |  |  |  |

For the payloads for other messages, see ref 4.

# HMI incoming Message data type

The data type to handle incoming messages from the main board is defined in mcb.c and depicted below:

// NVHR message

// --------------------------------------------------------------------------

typedef struct CPL_ATTRIB_PACKED MCB_msg_t

{

// standard message header (FROM mainboard)

uint8 msg_num; // 0 to 255 rolling

uint8 msg_type;

uint8 fw_ver;

uint8 serial[4]; // 32bit big endian

uint8 op_mode;

uint8 override_src;

uint8 fresh_damper_status;

uint8 window_advice_state;

uint8 season;

uint8 graph_state;

uint8 sub_mode;

uint8 fresh_fan_state;

uint8 recirc_fan_state;

uint8 current_override;

uint8 exhaust_damper_status;

uint8 bms_stop_source;

uint8 diag_code;

uint8 warn_code;

uint8 remote_override_time_req[2];

uint8 remote_override_time_rem[2];

uint8 remote_override_source;

uint8 boards_fitted;

uint8 ls_status;

uint8 switch_status;

uint8 port_output_bits;

uint8 usb_status;

uint8 rtc_hours;

uint8 rtc_minutes;

uint8 rtc_second;

// payload depends upon msg_type;

uint8 payload[64];

// 16bit additive checksum

uint8 chksum_msb;

uint8 chksum_lsb;

} MCB_msg_t;

All the incoming messages are handled by 
	bool_t   mcb_handle_msg(MCB_msg_t const* msg)    defined in mcb.c

# Messages to the main board

# Message types

Currently the following message types are supported – defined in mcb_config.h

// message type - incoming

#define MCB_MESSAGE_STANDARD_REPLY          100  // standard reply header values no payload

#define MCB_MESSAGE_CLOCKSET                101  // clockset

#define MCB_MESSAGE_COMMISSIONING           102  // air flow that the fans run at in payload

#define MCB_MESSAGE_CONTROLLED_MODE         103  // takes over control

#define MCB_MESSAGE_EE_WRITE                104  // <name> value(s)/array(s) in payload

#define MCB_MESSAGE_SENSOR_OVERRIDE         105  // override a sensor input

#define MCB_MESSAGE_LOAD_PRESET_FLOWS       106

#define MCB_MESSAGE_RESTORE_DEFAULTS        107  //

#define MCB_MESSAGE_USB                     108  // read write on payload

#define MCB_MESSAGE_NUMBER_OF_TYPES         109  // reduced normal or extended

#define MCB_MESSAGE_BMS_STOP                111  // NOT used by HMI

#define MCB_MESSAGE_BMS_START               112  // NOT used by HMI

#define MCB_MESSAGE_RESET_SERVICE           114

#define MCB_MESSAGE_MANUAL_OVERRIDE         115

#define MCB_MESSAGE_ACK                     		 255

# Message Body

| Byte | Message Type | Length | Field | Description |
| --- | --- | --- | --- | --- |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE STANDARD REPLY (100) |
| 2 |  | 1 | Not used | 0 |
| 3 |  | 1 | Not used | 0 |
| 4 |  | 1 | Not used | 0 |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | 8 | Peripheral Status | Meaning varies depending on peripheral |
| 11 |  |  |  |  |
| 12 |  |  |  |  |
| 13 |  |  |  |  |
| 14 |  |  |  |  |
| 15 |  |  |  |  |
| 16 |  |  |  |  |
| 17 |  |  |  |  |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |

| Byte | Message Type | Length | Field | Description |
| --- | --- | --- | --- | --- |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE CLOCKSET (101) |
| 2 |  | 1 | Not used | 0 |
| 3 |  | 1 | Not used | 0 |
| 4 |  | 1 | Not used | 0 |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | 1 | Minute | 0..59 ¦ Set bit 7 to set clock |
| 11 |  | 1 | Hour | 0..23 |
| 12 |  | 1 | Day of Month | 1..31 |
| 13 |  | 1 | Month | 1..12 |
| 14 |  | 1 | Day of Week | Not used (set to 1) |
| 15 |  | 1 | Year | 15..99 |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |

| Byte | Message Type | Length | Field | Description |
| --- | --- | --- | --- | --- |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE_COMMISSIONING (102) |
| 2 |  | 1 | Not used | 0 |
| 3 |  | 1 | Not used | 0 |
| 4 |  | 1 | Verification code | MESSAGE_COMMISSIONING_NUMBER (2) |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | 2 | Parent Fresh AF | MSB (0..1000 = 0.0-100.0%) |
| 11 |  |  |  | LSB |
| 12 |  | 2 | Parent Recirc AF | MSB (0..1000 = 0.0-100.0%) |
| 13 |  |  |  | LSB |
| 14 |  | 2 | Child Fresh AF | MSB (0..1000 = 0.00-10.00V) |
| 15 |  |  |  | LSB |
| 16 |  | 2 | Child Recirc AF | MSB (0..1000 = 0.00-10.00V) |
| 17 |  |  |  | LSB |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |

| Byte | Message Type | Length | Field | Description |
| --- | --- | --- | --- | --- |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE CONTROLLED MODE (103) |
| 2 |  | 1 | Not used |  |
| 3 |  | 1 | Verification code | MESSAGE_CONTROLLED_MODE_CODE (238) |
| 4 |  | 1 | Verification number | MESSAGE_CONTROLLED_MODE_NUMBER (5) |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | 1 | Fresh Damper State | TBC |
| 11 |  | 1 | Exhaust Damper State | TBC |
| 12 |  | 1 | Fresh fan-speed | 0=stopped, 1=starting, 2=min, 3=slow, 4=fast, 5=ultra |
| 13 |  | 1 | Recirc fan-speed |  |
| 14 |  | 1 | Window Advice | TBC |
| 15 |  | 1 | Season | TBC |
| 16 |  | 1 | Sub-mode | TBC |
| 17 |  | 2 | Voltage controlled Damper (0.0-100.0%) | MSB |
| 18 |  |  |  | LSB |
| 19 |  | 1 | Output freeze bits | bit 1=FanL, 2=FanR, 3=V1, 4=V2, 5=Relays, 6=H-Bridge (bits 7+8 spare) |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |

| Byte | Message Type | Length | Field | Description |
| --- | --- | --- | --- | --- |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE EE WRITE (104) |
| 2 |  | 1 | Not used | 0 |
| 3 |  | 1 | Num of Arrays | 1..4 for arrays, 0 for values |
| 4 |  | 1 | Num of Values | 1..18 for values, 0 for arrays |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | See command arrays & values sheet for details |  |  |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |

| Byte | Message Type | Length | Field | Description |
| --- | --- | --- | --- | --- |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE OVERRIDE_SENSOR (105) |
| 2 |  | 1 | Not used | 0 |
| 3 |  | 1 | Num of Arrays | 150 (magic value) |
| 4 |  | 1 | Num of Values | 0 |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | 1 | Sensor ID | TBC |
| 11 |  | 2 | Override Value | MSB |
| 12 |  |  |  | LSB |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |
| Byte | Message Type | Length | Field | Description |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE LOAD_PRESET_FLOWS (106) |
| 2 |  | 1 | Not used | 0 |
| 3 |  | 1 | Num of Arrays | MESSAGE_RESTORE_DEFAULTS_CODE (73) |
| 4 |  | 1 | Num of Values | 256 - MESSAGE_RESTORE_DEFAULTS_CODE |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | 1 | Preset number | 0=rectangular, 1=20pa spigot |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |

| Byte | Message Type | Length | Field | Description |
| --- | --- | --- | --- | --- |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE RESTORE DEFAULTS (107) |
| 2 |  | 1 | Not used | 0 |
| 3 |  | 1 | Num of Arrays | MESSAGE_RESTORE_DEFAULTS_CODE (73) |
| 4 |  | 1 | Num of Values | 256 - MESSAGE_RESTORE_DEFAULTS_CODE |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | None |  |  |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |
| Byte | Message Type | Length | Field | Description |
| 0 | Header | 1 | Message Number | Cycles 0..255 |
| 1 |  | 1 | Message Type | MESSAGE USB (108) |
| 2 |  | 1 | Not used | 0 |
| 3 |  | 1 | Not used | 0 |
| 4 |  | 1 | Not used | 0 |
| 5 |  | 1 | Message types | 0=normal, 1=extended, other=reduced |
| 6 |  | 1 | Spare |  |
| 7 |  | 1 | Spare |  |
| 8 |  | 1 | F/W Ver High | 0..255 (0=pre-release, 1=first major release) |
| 9 |  | 1 | F/W Ver Low | 0..255 |
| 10 | Payload | 1 | USB Command | TBC |
| 82 | Footer | 2 | Checksum | MSB |
| 83 |  |  |  | LSB |

Further details and messages are described in ref 4 document.

# HMI outgoing Message data type

The following data type defines the outgoing messages, specified as:

// --------------------------------------------------------------------------

typedef struct CPL_ATTRIB_PACKED MCB_reply_t

{

// standard message header (TO mainboard)

uint8 msg_num; // cycles round 1 to 255

uint8 msg_type;

uint8 btn_value;

uint8 num_arrays;

uint8 num_values;

uint8 message_types; // 0 to 9 (tbc) or 46 if not yet adjusted

uint8 remote_onoff;

uint8 spare;

uint8 fw_ver_major;

uint8 fw_ver_minor;

// payload depends upon msg_type;

uint8 payload[72];

// 16bit additive checksum

uint8 chksum_msb;

uint8 chksum_lsb;

} MCB_reply_t;

All the outgoing messages are handled by the function:
	bool_t  mcb_prepare_prog(MCB_reply_t * reply)  defined in mcb.c file.

# VAR module

HMI and the Mainboard convey data through global variable set (VAR). They are classified in file var.h as:

VAR_TABLE_STAT.
VAR_TABLE_SINK,
VAR_TABLE_INTERN,
VAR_TABLE_EE

To read from these variables,  var_data_all-> is de-referenced.
To write to these variables, VAR_prog_u8(VAR_ID_var, value), VAR_prog_u16(VAR_ID_var, value), VAR_prog_u32(VAR_ID_var, value) are utilised.

# VAR functionality

# NVHR Vars

# NVHR 16 bit EEPROM Memory Map

| EE Hex | EE Dec | Name | Description | Write | Var Name | Msg |
| --- | --- | --- | --- | --- | --- | --- |
| Working Block – 16 bit values |  |  |  |  |  |  |

Working Block – 16 byte Arrays

Machine Setup – 16 bit Values

Machine Setup – 16 byte Arrays

PCB Calibration – 16 bit Values

# HMI Software Modules

The main entry to the NVHR HMI system is through the home screen. Any changes to the system may be carried out through the settings option.

# Home screen splash

The following screen shall contain the specified controls derived from the workflow, allowing the user navigation and access to system maintenance, setup (commissioning) and the system information.

# Home screen logic

| VentManualOp | Override Source | Info Display | Auto Vent | More Vent | Disable Vent | Max Vent |
| --- | --- | --- | --- | --- | --- | --- |
| AUTO | NONE (no others should ever show) | Window Advice | Highlighted Not clickable | Not highlighted Clickable | Not highlighted Clickable | Not highlighted Clickable |
| MANUAL_MORE_VENT | BUTTON_P1_to_6 (HMI) | Countdown | Not highlighted Clickable | Highlighted Not clickable | Not highlighted Clickable | Not highlighted Clickable |
| MANUAL_MORE_VENT | (any other) | Override source | Not highlighted Not clickable | Highlighted Not clickable | Not highlighted Clickable | Not highlighted Clickable |
| MANUAL_DISABLE_VENT | BUTTON_P1_to_6 (HMI) | Countdown | Not highlighted Clickable | Not highlighted Clickable | Highlighted Not clickable | Not highlighted Clickable |
| MANUAL_DISABLE_VENT | STOP_SW1 STOP_DIAGNOSTIC STOP_FAULT_CODE STOP_SETUP_OFF STOP_BMS | OFF |  |  |  |  |
| MANUAL_DISABLE_VENT | (any other) | Override source | Not highlighted Not clickable | Not highlighted Clickable | Highlighted Not clickable | Not highlighted Clickable |
| MANUAL_MAX_VENT | BUTTON_P1_to_6 (HMI) | Countdown | Not highlighted Clickable | Not highlighted Clickable | Not highlighted Clickable | Highlighted Not clickable |
| MANUAL_MAX_VENT | (any other) | Override source | Not highlighted Not clickable | Not highlighted Clickable | Not highlighted Clickable | Highlighted Not clickable |
| ACTIVE_NIGHT_COOL PASSIVE_NIGHT_COOL | NONE (no others should ever show) | Night Cooling | Highlighted Not clickable | Not highlighted Clickable | Not highlighted Clickable | Not highlighted Clickable |
| REMOTE_CONTROLLED COMMISSIONING DIAGNOSTICS (any other / undefined) | (any) | VentManualOp Name | Not highlighted Not clickable | Not highlighted Not clickable | Not highlighted Not clickable | Not highlighted Not clickable |

# HMI software components

The following diagram depicts the stereotyped software components of the HMI subsystem.

Each component package will be described in further details in the following sections. The function prototypes and data structures are specified in file scr.h

# HMI User_display

| Public Method | Description | Data Structure |
| --- | --- | --- |
| void NVHR_SCR_screen_user_display(void) | Sets display to ON or OFF |  |
| void NVHR_SCR_screen_user_display_off(void) | Sets display to OFF state. Also used in Home Screen Logic and tick functions | typedef struct NVHR_SCR_screen_user_display_off_t { TButton_Round nvhr_message; TButton nvhr_settings; } NVHR_SCR_screen_user_display_off_t; |
| void NVHR_SCR_screen_user_display_on(void) | Sets display to ON state. Also used in Home Screen Logic and tick functions | typedef struct NVHR_SCR_screen_user_display_t { TButton_Round nvhr_auto; TButton_Round nvhr_boost; TButton_Round nvhr_sleep; TButton_Round nvhr_maxvent; TButton_Round nvhr_co2; TButton_Round nvhr_temperature; TButton_Round nvhr_info_display; TButton nvhr_settings; SCR_custom_t nvhr_auto_right_arrow; SCR_custom_t nvhr_boost_right_arrow; SCR_custom_t nvhr_maxvent_right_arrow; SCR_custom_t nvhr_sleep_right_arrow; SCR_custom_t nvhr_triangle; } NVHR_SCR_screen_user_display_t; |
| void NVHR_SCR_boost_settings(uint32 index) | Sets boost times. Index determines if for maxvent, boost or sleep | typedef struct NVHR_SCR_boost_settings_t { TCircleButton nvhr_help; TButton nvhr_title; TButton_Round nvhr_time1; TButton_Round nvhr_time2; TButton_Round nvhr_time3; TButton_Round nvhr_time4; SCR_custom_t nvhr_back; SCR_custom_t nvhr_time1_right_arrow; SCR_custom_t nvhr_time2_right_arrow; SCR_custom_t nvhr_time3_right_arrow; SCR_custom_t nvhr_time4_right_arrow; } NVHR_SCR_boost_settings_t; |
| void NVHR_SCR_boost_help(void) | Boost help screen | typedef struct NVHR_SCR_help_struct_t { TButton nvhr_title; TButton_Round nvhr_help_bg; SCR_custom_t nvhr_back; TLabel nvhr_help_lbl[SCR_VLIST_MAX_ROWS]; char nvhr_help_txt[SCR_VLIST_MAX_ROWS][42]; } NVHR_SCR_help_t; |

# HMI Settings (User_settings)

| Public Method | Description | Data Structure |
| --- | --- | --- |
| void NVHR_SCR_screen_user_settings(void) | The user settings sub-menu | typedef struct NVHR_SCR_screen_user_settings_struct { TButton title; SCR_custom_t back; SCR_vlist_t vlist; char strings[SCR_VLIST_MAX_ROWS][16]; } NVHR_SCR_screen_user_settings_t; |

# HMI User Maintenance

| Public Method | Description | Data Structure |
| --- | --- | --- |
| void NVHR_SCR_user_maintenance(void) | The user Maintenance sub-menu | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_user_maintenance_t; |

# HMI User Setup

| Public Method | Description | Data Structure |
| --- | --- | --- |
| void NVHR_SCR_user_setup(void) | The user Setup sub-menu | typedef struct NVHR_SCR_user_setup_struct { TButton title; SCR_custom_t back; SCR_vlist_t vlist; char strings[SCR_VLIST_MAX_ROWS][16]; } NVHR_SCR_user_setup_t; |

# HMI Common

| Public Method | Description | Data Structure |  |
| --- | --- | --- | --- |
| void NVHR_SCR_screen_lock_code(void) | Used for locking screen – not utilised | typedef struct SCR_screen_lock_code_struct { SCR_screen_adjuster_quad_t a; TButton done; } SCR_screen_lock_code_t; |  |
| void NVHR_SCR_screen_unlock(uint8 index); | Used for unlocking screen – quad adjuster |  |  |
| void NVHR_SCR_system_on_off(void) | Toggle screen | typedef struct SCR_screen_chklist_struct { TButton title; TButton action; SCR_custom_t action_arrow; SCR_custom_t back; SCR_custom_t next; SCR_chklist_t chklist; uint8 indices[SCR_CHKLIST_MAX_ROWS]; char strings[SCR_CHKLIST_MAX_ROWS][32]; } NVHR_SCR_screen_system_on_off_t; |  |
| void NVHR_SCR_system_yes_no(void); | Toggle screen | typedef struct SCR_screen_chklist_struct { TButton title; TButton action; SCR_custom_t action_arrow; SCR_custom_t back; SCR_custom_t next; SCR_chklist_t chklist; uint8 indices[SCR_CHKLIST_MAX_ROWS]; char strings[SCR_CHKLIST_MAX_ROWS][32]; } NVHR_SCR_screen_system_yes_no_t; |  |
| void NVHR_SCR_screen_display_settings(void); | Single adjuster for display settings | typedef struct SCR_screen_adjuster_single_struct { // Widgets TButton title; TCircleButton nvhr_help; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t value; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_single_struct* a); } SCR_screen_display_settings_t; |  |
| void NVHR_SCR_screen_address_settings(void) | Single adjuster for address settings | typedef struct SCR_screen_adjuster_single_struct { // Widgets TButton title; TCircleButton nvhr_help; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t value; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_single_struct* a); } NVHR_SCR_screen_address_settings_t |  |
| void NVHR_SCR_test_sequence(void) | Test sequence screens | typedef struct NVHR_SCR_test_sequence_t { TButton title; TButton_Round message1_container; TButton_Round confirm; TButton_Round cancel; SCR_custom_t back; TLabel test_sequence_lbl[SCR_VLIST_MAX_ROWS]; char test_sequence_txt[SCR_VLIST_MAX_ROWS][40]; } NVHR_SCR_test_sequence_t; |  |
| void NVHR_SCR_option_unavailable(void) | Screen for unavailable options | typedef struct NVHR_SCR_not_done_t { TButton title; TButton_Round message_container; TButton_Round confirm; TLabel not_done_lbl[SCR_VLIST_MAX_ROWS]; char not_done_txt[SCR_VLIST_MAX_ROWS][40]; } NVHR_SCR_not_done_t; |  |
| void NVHR_SCR_display_settings(void) | Display brightness settings | typedef struct SCR_screen_adjuster_single_struct { // Widgets TButton title; TCircleButton nvhr_help; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t value; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_single_struct* a); } SCR_screen_display_settings_t; |  |
| void NVHR_SCR_room_temp_setpoint(void); | Adjuster for room temperature setpoint | typedef struct SCR_screen_adjuster_single_struct { // Widgets TButton title; TCircleButton nvhr_help; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t value; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_single_struct* a); } NVHR_SCR_temp_setpoint_t; |
| void NVHR_SCR_room_temp_setpoint_help(void); | Help screen | typedef struct NVHR_SCR_help_struct_t { TButton nvhr_title; TButton_Round nvhr_help_bg; SCR_custom_t nvhr_back; TLabel nvhr_help_lbl[SCR_VLIST_MAX_ROWS]; char nvhr_help_txt[SCR_VLIST_MAX_ROWS][42]; } NVHR_SCR_room_temp_setpoint_help_t; |
| void NVHR_SCR_winsum_xover(void) | Winter to Summer cross over | typedef struct SCR_screen_adjuster_single_struct { // Widgets TButton title; TCircleButton nvhr_help; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t value; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_single_struct* a); } NVHR_SCR_temp_setpoint_t; |
| void NVHR_SCR_winsum_xover_help(void) | Help screen for Winter Summer crossover | typedef struct NVHR_SCR_help_struct_t { TButton nvhr_title; TButton_Round nvhr_help_bg; SCR_custom_t nvhr_back; TLabel nvhr_help_lbl[SCR_VLIST_MAX_ROWS]; char nvhr_help_txt[SCR_VLIST_MAX_ROWS][42]; } NVHR_SCR_room_temp_setpoint_help_t; |
| void NVHR_SCR_common_sysinfo(void) | System info for Maintenance and Setup | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_common_sysinfo_t; |
| void NVHR_SCR_common_sysinfo_readme(void) | Help screen for system info | typedef struct NVHR_SCR_system_info_readme_t { TButton nvhr_title; TButton_Round nvhr_help_bg; SCR_custom_t nvhr_back; TLabel nvhr_help_lbl[SCR_VLIST_MAX_ROWS]; char nvhr_help_txt[SCR_VLIST_MAX_ROWS][32]; } NVHR_SCR_system_info_readme_t; |
| void NVHR_SCR_screen_common_sysinfo_about(void) | Info about sysinfo | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_common_sysinfo_about_t; |
| void NVHR_SCR_common_setpoints(void) | Setpoints screen for Maintenance and Setup | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_common_setpoints_t; |
| Void NVHR_SCR_common_sensor_readings(void) | Sensor readings | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_sensor_readings_t; |
| void NVHR_SCR_common_fandamp_status(void) | Fan and Damper status for Maintenance and Setup | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_common_fandamp_t; |
| void NVHR_SCR_common_timedate_settings(void) | Time and date settings | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_common_datetime_t; |
| void NVHR_SCR_common_userscr_settings(void) | User settings sub-menu | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_common_userscr_t; |
| void NVHR_SCR_common_notices(void) | Notices screen | Option unavailable |
| void NVHR_SCR_screen_date(void) | Date setup widget | typedef struct NVHR_SCR_screen_date_struct { TButton title; SCR_custom_t back; TButton_Round inc_year; TButton_Round inc_month; TButton_Round inc_day; TButton_Round dec_year; TButton_Round dec_month; TButton_Round dec_day; TLine line1; TLine line2; TButton year_title; TButton month_title; TButton day_title; TButton year_value; TButton month_value; TButton day_value; char str_year[8]; char str_month[8]; char str_day[8]; uint8 date_year; uint8 date_month; uint8 date_day; } NVHR_SCR_screen_date_t; |
| void NVHR_SCR_screen_time(void) | Time setup widget | typedef struct NVHR_SCR_screen_time_struct { TButton title; SCR_custom_t back; TButton_Round inc_hour; TButton_Round inc_mins; TButton_Round dec_hour; TButton_Round dec_mins; TLine line1; TLine line2; TButton hour_title; TButton mins_title; TButton hour_value; TButton mins_value; TLabel separator; char str_hour[8]; char str_mins[8]; uint8 time_hour; uint8 time_mins; } NVHR_SCR_screen_time_t; |
| void NVHR_SCR_occupied_days_hours(void) | Widget to specify occupied days and hours | typedef struct NVHR_SCR_common_date_t { SCR_screen_vlist_t vscr; SCR_weekdays_t weekdays; char time_str[16]; } NVHR_SCR_common_date_t; |
| void NVHR_SCR_nightcool_days_hours(void) | Widget to specify nightcool days and hours | typedef struct NVHR_SCR_common_date_t { SCR_screen_vlist_t vscr; SCR_weekdays_t weekdays; char time_str[16]; } NVHR_SCR_common_date_t; |
| void NVHR_SCR_nightcool_period(void) | Dual adjuster to specify nightcool period | typedef struct SCR_screen_adjuster_dual_struct { // Widgets TButton title; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster[2]; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t values[2]; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_dual_struct* a, uint8 index); } NVHR_SCR_nightcool_period_t; |
| void NVHR_SCR_common_bacnet(void) | BACnet subsystem menu | typedef struct NVHR_SCR_common_bacnet_modbus_struct { TButton title; SCR_custom_t back; SCR_vlist_t vlist; char strings[SCR_VLIST_MAX_ROWS][16]; } NVHR_SCR_common_bacnet_modbus_t; |
| void NVHR_SCR_common_network_baud(void) | Setup baud rate | typedef struct SCR_screen_chklist_struct { TButton title; TButton action; SCR_custom_t action_arrow; SCR_custom_t back; SCR_custom_t next; SCR_chklist_t chklist; uint8 indices[SCR_CHKLIST_MAX_ROWS]; char strings[SCR_CHKLIST_MAX_ROWS][32]; } NVHR_SCR_common_network_baud_t; |
| void NVHR_SCR_common_modbus(void) | Modbus subsystem menu | typedef struct NVHR_SCR_common_bacnet_modbus_struct { TButton title; SCR_custom_t back; SCR_vlist_t vlist; char strings[SCR_VLIST_MAX_ROWS][16]; } NVHR_SCR_common_bacnet_modbus_t; |
| void NVHR_SCR_screen_common_modbus_parity(void) | Checklist for parity setup | typedef struct SCR_screen_chklist_struct { TButton title; TButton action; SCR_custom_t action_arrow; SCR_custom_t back; SCR_custom_t next; SCR_chklist_t chklist; uint8 indices[SCR_CHKLIST_MAX_ROWS]; char strings[SCR_CHKLIST_MAX_ROWS][32]; } NVHR_SCR_common_network_parity_t; |
| void NVHR_SCR_common_fans(void) | Fan setup menu | typedef struct NVHR_SCR_common_fandamp_struct { TButton title; SCR_custom_t back; SCR_vlist_t vlist; char strings[SCR_VLIST_MAX_ROWS][16]; } NVHR_SCR_common_fan_damp_t; |
| void NVHR_SCR_common_dampers(void) | Damper setup menu | typedef struct NVHR_SCR_common_fandamp_struct { TButton title; SCR_custom_t back; SCR_vlist_t vlist; char strings[SCR_VLIST_MAX_ROWS][16]; } NVHR_SCR_common_fan_damp_t; |
| void NVHR_SCR_screen_service_input(char const *title, VAR_phone_num_t const *ph) | Service input widget | typedef struct SCR_screen_service_phone_t { TButton title; SCR_custom_t back; SCR_custom_t next; SCR_custom_t phone; TButton_Round btn_left; TButton_Round btn_right; TButton_Round btn_digit[12]; char str_digit[12][2]; SCR_event_handler_t evt_handler; uint8 active_digit; VAR_phone_num_t phone_num; } SCR_screen_service_phone_t; |
| void SCR_screen_invalid_defaults(void) | Error message dialog | typedef struct SCR_screen_error_t { TButton title; SCR_custom_t back; TButton info1; TButton info2; } SCR_screen_error_t; |
| void NVHR_SCR_screen_invalid_model(void) | Error message dialog | typedef struct SCR_screen_error_t { TButton title; SCR_custom_t back; TButton info1; TButton info2; } SCR_screen_error_t; |
| void NVHR_SCR_vent_on_CO2(void) | Dual adjuster for Vent on CO2 | typedef struct SCR_screen_adjuster_dual_struct { // Widgets TButton title; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster[2]; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t values[2]; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_dual_struct* a, uint8 index); } NVHR_SCR_screen_vent_on_CO2_t; |
| void NVHR_SCR_room_CO2_indicator(void) | Dual adjuster for CO2 low and CO2 high | N typedef struct SCR_screen_adjuster_dual_struct { // Widgets TButton title; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster[2]; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t values[2]; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_dual_struct* a, uint8 index); } NVHR_SCR_screen_rm_co2_indicator_t; |
| void NVHR_SCR_winter_offset(void) | Single adjuster for winter offset temperature | typedef struct SCR_screen_adjuster_single_struct { // Widgets TButton title; TCircleButton nvhr_help; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t value; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_single_struct* a); } NVHR_SCR_winter_offset_setpoint_t; |
| void NVHR_SCR_nightcool_trigger(void) | Dual adjuster for Day max setpoint and room temp point | typedef struct SCR_screen_adjuster_dual_struct { // Widgets TButton title; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster[2]; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t values[2]; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_dual_struct* a, uint8 index); } NVHR_SCR_screen_nightcool_trigger_t; |
| void NVHR_SCR_mixed_delivery(void) | List of mixed delivery items – temp set point and PID control constants | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_mixed_air_delivery_t; |
| void NVHR_SCR_air_delivery_temp(void) | Single adjuster for air delivery temperature set point | typedef struct SCR_screen_adjuster_single_struct { // Widgets TButton title; TCircleButton nvhr_help; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t value; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_single_struct* a); } NVHR_SCR_air_delivery_temp_t; |
| void NVHR_SCR_air_delivery_pid(void) | Triple adjuster for Kp, Ki and Kd coefficients (+/- 373) | typedef struct SCR_screen_adjuster_triple_struct { // Widgets TButton title; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster[3]; TLine line1; TLine line2; // Data uint16 tag; uint16 tag2; SCR_adjuster_value_t values[3]; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_triple_struct* a, uint8 index); } NVHR_SCR_air_delivery_pid_t; |
| void NVHR_SCR_fan_speeds(void) | The menu lists for Fan speed setup | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_fan_speed_t; |
| Static void nvhr_scr_fan_single_speed(uint8_t index, const char * title) | Dual adjusters for parent fresh (PF) setting up (following index): STARTING MINIMUM WINTER_SLOW WINTER_FAST SUMMER_SLOW SUMMER_FAST ULTRA | typedef struct SCR_screen_adjuster_single_struct { // Widgets TButton title; TCircleButton nvhr_help; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t value; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_single_struct* a); } NVHR_SCR_screen_fan_single_speed_t; |
| static void nvhr_scr_fan_dual_speed(uint8 index, const char * title) | Dual adjusters for parent-child fresh (PF – CF) setting up (following index): STARTING MINIMUM WINTER_SLOW WINTER_FAST SUMMER_SLOW SUMMER_FAST ULTRA | typedef struct SCR_screen_adjuster_dual_struct { // Widgets TButton title; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster[2]; TLine line1; TLine line2; // Data uint16 tag; SCR_adjuster_value_t values[2]; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_dual_struct* a, uint8 index); } NVHR_SCR_screen_fan_dual_speed_t; |
| void NVHR_SCR_override_durations(uint8 index) | Override durations setup with End-of-day: Duration1 Duration2 Duration3 Duration4 with E-O-D | typedef struct SCR_screen_adjuster_triple_struct { // Widgets TButton title; SCR_custom_t back; SCR_custom_t next; SCR_adjuster_t adjuster[3]; TLine line1; TLine line2; // Data uint16 tag; uint16 tag2; SCR_adjuster_value_t values[3]; // Events // This is not only for notifications but it is also // required for formatting of display strings. // Otherwise no values will be displayed. SCR_event_handler_t evt_handler; void(*changed)(struct SCR_screen_adjuster_triple_struct* a, uint8 index); } NVHR_SCR_override_durations_t; |
| void NVHR_SCR_fan_dual_speed_perform(uint8 index) | Calls - 2 speeds nvhr_scr_fan_dual_speed() with index: STARTING MINIMUM WINTER_SLOW WINTER_FAST SUMMER_SLOW SUMMER_FAST ULTRA |  |
| void NVHR_SCR_fan_single_speed_perform(uint8 index) | Calls – 1 speed nvhr_scr_fan_single_speed() with index: STARTING MINIMUM WINTER_SLOW WINTER_FAST SUMMER_SLOW SUMMER_FAST ULTRA |  |
| uint8 NVHR_SCR_translate_fan_to_mcb_speed(uint8 fan_speed_index ) | Convenient function returning equivalent MCB speed enumeration given the fan_speed_index: STARTING => WS_STARTING MIN => WS_MIN WINT_SLOW => WINTER_SLOW WINT_FAST => WINTER_FLAST SUM_SLOW => SUMMER_SLOW SUM_FAST => SUMMER_FAST ULTRA => WS_ULTRA |  |

# HMI System_info

| Public Method | Description | Data Structure |
| --- | --- | --- |
| void NVHR_SCR_system_info(void) | The screens for user information display | typedef struct SCR_screen_vlist_ex_struct { SCR_screen_vlist_t vscr; char strings[SCR_VLIST_MAX_ROWS][32]; uint8 indices[SCR_VLIST_MAX_ROWS]; uint8 user; } NVHR_SCR_screen_system_info_t; |

# Summary

In this document, only the HMI’s public functions (with exception of nvhr_scr_fan_single_speed () and nvhr_scr_fan_dual_speed () private functions) prototyped in scr.h are covered.

# Further Work Recommendations

- Provide Logging mechanism.

- Provide a facility to distinguish Errors/Exceptions/Warnings/Information and
depict them in HMI accordingly. This should give the user a better understanding
of the nature issue flagged by the HMI system.

- Support other messages not covered yet (Defined in  mcb_config.h):

  - MCB_MESSAGE_EE_ARRAYS_2

  - MCB_MESSAGE_EE_ARRAYS_3

  - MCB_MESSAGE_EE_ARRAYS_4

  - MCB_MESSAGE_EE_ARRAYS_5

  - MCB_MESSAGE_EE_ARRAYS_6

  - MCB_MESSAGE_EE_ARRAYS_7

  - MCB_MESSAGE_EE_ARRAYS_8

- Provide mechanism for setting user pin code.

# HMI Build Tools

- MikroC Pro for PIC32 IDE and development environment – Version 4.0.0 
From www.mikroe.com

- MPLAB IPE V.4.05 (Integrated Programming Environment)

- MPLAB ICD3 for firmware transfer to the HMI board

- HMI board with PIC32MX460F512L device

- SVN code repository

# HMI Build Process

- Make sure the MikroC Pro project nvhrAdvanceHmi.mcp32 exists

- Compile and build the project using the MikroC Pro

- If successful, then <project>.hex is created (nvhrAdvanceHmi.hex)

- In IPE, select device PIC32MX460F512L

- In IPE, Connect to ICD3 (e.g.  ICD 3 S.No: JIT171610281)

- In IPE, Browse and select nvhrAdvanceHmi.hex file from a pre-defined location

- In IPE, Program the device

- In IPE, make sure Settings->Release from Reset is selected

- The HMI board should now be loaded with the new firmware

# Appendix A – NVHR HMI Screens Workflow

The following user requirement diagram shows the fundamental user interaction flow blocks of BB NVHR HMI.

This includes User, Maintenance, and commissioning screens, colour coded (Blue for User, Green for Maintenance and Red for Commissioning).

User Menu

| Landing Menu |  |  |  |
| --- | --- | --- | --- |
| Auto * |  |  |  |
| Boost > | Boost Menu |  |  |
|  | 30 min |  |  |
|  | 1 hr |  |  |
|  | 2 hr |  |  |
|  | End of Day |  |  |
| Sleep > | Sleep Menu |  |  |
|  | 30 min |  |  |
|  | 1 hr |  |  |
|  | 2 hr |  |  |
|  | End of Day |  |  |
| Max Vent > | Max Vent Menu |  |  |
|  | 30 min |  |  |
|  | 1 hr |  |  |
|  | 2 hr |  |  |
|  | End of Day |  |  |
| Settings > | Settings Menu |  |  |
|  | System Info > | System Info Menu |  |
|  |  | Date & Time |  |
|  |  | Unit Status |  |
|  |  | Mode |  |
|  |  | Unit Activity |  |
|  |  | Room Temp |  |
|  |  | Room CO2 |  |
|  |  | Room Temp Setpoint > | RT Set Point |
|  |  |  | Room Temp Set Point Adj |
|  |  | External Temp |  |
|  |  | About |  |
|  | Screen Options > | Screen Option |  |
|  |  | Brightness Adjust |  |
|  | Maintenance > |  |  |
|  |  | Maintenance Pin |  |
|  |  | Enter Pin > |  |
|  |  |  | Maintenance Menu |
|  | Setup > | Setup Pin |  |
|  |  | Enter Pin > |  |
|  |  |  | Setup Menu |

| Maintenance Menu |  |  |  |
| --- | --- | --- | --- |
| On/Off/Test> | On/Off/Test Menu |  |  |
|  | On |  |  |
|  | Off |  |  |
|  |  | Off Screen |  |
|  | Test Sequence> |  |  |
|  |  | Test Confirmation Menu |  |
|  |  | Cancel |  |
|  |  | Confirm | Test1 |
|  |  |  | Cancel |
|  |  |  | Test2 |
|  |  |  | Cancel |
|  |  |  | Test3 |
|  |  |  | Cancel |
| System Info > | System Info Menu |  |  |
|  | Unit Status: |  |  |
|  | Mode: |  |  |
|  | Unit Activity: |  |  |
|  | Configuration: |  |  |
|  | About | About Information Screen |  |
|  |  | Project No.: |  |
|  |  | Setup Date: |  |
|  |  | NVHR Model: |  |
|  |  | Hardware Version: |  |
|  |  | Firmware Version: |  |
|  |  | Parent S/N: |  |
|  |  | Child S/N: |  |
|  |  | Network ID: |  |
|  |  | Protocol: |  |
|  |  | Slave Address: |  |
|  |  | Read Me> | Read Me Screen |
| Sensor Readings> | Sensor Readings Screen |  |  |
|  | External Temp: |  |  |
|  | Room Temp: |  |  |
|  | Room CO2: |  |  |
|  | Delivery Temp: |  |  |
|  | Exhaust Temp: |  |  |
| Fan & Damper Status> | Fan & Damper Menu |  |  |
|  | Fans> | Fan Information screen |  |
|  |  | Parent Fresh: |  |
|  |  | Child Fresh: |  |
|  | Dampers> | Damper Info Screen |  |
|  |  | Fresh Damper: |  |
| Set Points> | Set Point Menu |  |  |
|  | Vent On Room Temp: |  |  |
|  | Winter Sum Xover: |  |  |
|  | Vent On Room CO2 |  |  |
|  | Winter Offset |  |  |
|  | Temp Trigger: |  |  |
| Time & Date Settings | Time & Date Menu |  |  |
|  | Time > | Time Adj Screen |  |
|  |  | Hour |  |
|  |  | Min |  |
|  | Date > | Date Adj Screen |  |
|  |  | Year YYYY (+/-) |  |
|  |  | Month MM (+/-) |  |
|  |  | Day DD (+/-) |  |
|  | User Screen Options> | User Screen Options Menu |  |
|  |  | Allow Max Vent |  |
|  |  | All Room Override |  |
|  |  | Allow Room Temp Adj |  |
|  | Network Information > | BACnet Info Screen |  |
|  |  | Baud Rate |  |
|  |  | MAC Address |  |
|  |  | Modbus Info Screen |  |
|  |  | Slave Address |  |
|  |  | Baud Rate |  |
|  |  | Parity |  |
|  |  | Stop Bit |  |
|  | Notices > | Notices Menu |  |
|  |  | Fans> | Fan Error Screen |
|  |  | Dampers> | Damper Error Screen |
|  |  | Sensors > | Sensor Screen |
|  |  | Contact Details> | Contact Details Screen |
| Setup Menu |  |  |  |
| On/Off/Test | On/Off/Test Menu |  |  |
|  | Same as Maintenance |  |  |
| System Info > | System Info Menu |  |  |
|  | Unit Status: |  |  |
|  | Mode: |  |  |
|  | Unit Activity: |  |  |
|  | About > |  |  |
| Sensor Readings > | Same as Maintenance |  |  |
| Fan & Damper Status > | Same as Maintenance |  |  |
| Set Points > | Same as Maintenance |  |  |
|  | + Fan Speeds > | Fan Speed Set Points |  |
|  |  | Set Point F1 > | Fan Speed Adj Screen |
|  |  | Set Point F2 > | Parent Fresh Adj (+/-) |
|  |  | Set Point F3 > | Child Fresh Adj (+/-) |
|  |  | Set Point F4 > |  |
|  |  | Set Point F5 > |  |
|  |  | Set Point F6 > |  |
|  |  | Set Point F7 > |  |
|  |  | Set Point F8> |  |
|  | + Override Times | Set Override Durations |  |
|  |  | Duration 1 | Override Adj Screen |
|  |  | Duration 2 | hh adj (+/-) |
|  |  | Duration 3 | mm Adj (+/-) |
|  |  | Duration 4 / End of Day | End of Day Adj (Yes/No) |
| Time & Date Settings > | Same as Maintenance |  |  |
|  | + Occupied Days | Occupied Days Screen |  |
|  | +Night Cool Period | Night Cool Adj Screen |  |
|  | +HMI Screen Controls | HMI Screen Options Menu |  |
|  | +Network Information | BACnet Info screen |  |
|  |  | Modbus info screen |  |
|  | Notices > | Same as Maintenance |  |
|  | Reset | Reset to Factory Settings |  |

# Appendix B – NVHR HMI Screenshots

The following pages depict the screen shots captured from NVHR HMI application.

Source to be made available in maintenance / commissioning screens

In future update, with night cool cancellable, Auto is not highlighted and clickable to cancel (for a given period)